- Construction Management Checklist for Energizing Utilities

(Contractor to initial each item upon completion and provide completed

form to the Owner’s Represtentative prior to energizing utility)

Water – turned on to the first valve past EM’s last valve.

___  Review all piping and equipment being turned on for proper installation and completed testing.

___  Insulation installed (preferred but not required)

___  Meter properly installed, working, and in readable location.

___  Contractor has swabbed out with chlorine all piping from the backflow preventer to the source

while installing.

___  Backflow preventer installed and tested. (will need water pressure to test)

___  Pressure test completed in piping being turned on.

___  Contractor has method to communicate “Services On” to other contractor personnel and

Owner’s personnel.

Steam – turned on to the first valve past EM’s last valve.

___  Review all piping and equipment being turned on for proper installation and completed testing.

___  Piping protected from the weather.

___  Insulation must be installed.

___  Meter installed, working and in readable location. (Don’t need metasys to turn on.)

___  All needed traps are installed and able to be tested as they are turned on.

___  Condensate system is installed and operating including the pumping system.

___  Pressure test completed in piping being turned on.

___  Contractor has method to communicate “Services On” to other contractor personnel and

Owner’s personnel.

Condensate – turned on to the first valve past EM’s last valve.

___  Review all piping and equipment being turned on for proper installation and completed testing.

___  Piping protected from the weather.

___  Insulation installed (preferred but not required)

___  Pressure test completed in piping being turned on.

___  Contractor has method to communicate “Services On” to other contractor personnel and

Owner’s personnel.

Electric – turned on to the first breaker past 13.8kV transformer.

___  Review all wiring and equipment being turned on for proper installation and completed testing

___  GFCI set and tested.

___  Breakers set and tested.

___  All needed grounds are installed.

___  Meter installed, working and in readable location.

___  Main switchgear protected from the weather.

___  Contractor has method to communicate “Services On” to other contractor personnel and

Owner’s personnel.

Chilled Water – turned on to the first valve inside of building.

___  Review all piping and equipment being turned on for proper installation and completed testing.

___  Pressure test completed in piping being turned on.

___  Insulation must be installed.

___  Meter installed, working and connected to Metasys.

___  Building pump and automatic isolation/control valve must be installed and under control.

___  If chillers are installed, automatic loop pump isolation must be installed.

___  Control valves must be installed and automatically controlled on all loads.

___  Contractor has method to communicate “Services On” to other contractor personnel and

Owner’s personnel.